## Sheet1
This spreadsheet and its contents are provided for educational purposes only and are not intended to be used as professional or legal advice or services. The calculations, assumptions, and data contained within are illustrative and should be independently verified before being used for any real-world decision-making. Turbine Logic makes no warranties regarding the accuracy, reliability, or completeness of the information provided and will not be liable for any errors, omissions, or for any losses, injuries, or damages arising from its use or display. Users should exercise their own judgment and consult with a professional if required.
Capacity Factor | 55% | 12 month rolling average
Base Load rating | 300 | MW (Total rating for SC or CCGT (CTs + ST)
Configuration | 2 | CTs per Steam Turbine (enter 2 for 2-on-1). If Simple Cycle, enter 1
Base Load Heat Rate | 7800 | HHV (BTU/kWh)
Calculated Heat Input | 1170 | MMBTU/hr
Fuel Heat Input Based Emissions Rate | 120 | lb CO2/MMBTU
CO2 Standard | 847.4286 | lbm CO2/MWh
Required Heat Rate (12 month rolling average) | 7696.7869 | BTU/kWh -- HHV
Baseload Combustion Turbines (>40% Capacity Factor)
BLER_L | 800 | Baseload emissions standard for natural-gas fired combustion turbines with base load ratings greater than 2000 MMBTU/h
BLER_s | 900 | Base load emissions standard for natural-gas fired combustion turbines with base load rating of 250 MMBTU/h
BLR_L | 2000 | Minimum base load rating of large combustion turbines (2000 MMBTU/h)
BLR_s | 250 | Base load rating of smallest combustion turbine (250 MMBTU/h)
BLR_A | 1170 | Base load rating of the actual combustion turbine (MMBTU/h)
HIER_A | 120 | Heat input-based emissions rate of the actual fuel burned in the combustion turbine (lb CO2/MMBTU) - HHV Basis
HIER_NG | 120 | Heat input based emissions rate of natural gas (lb CO2 / MMBTU)
Intermediate Load Turbines (20% to 40% Capacity Factor)
ILER | 1170 | Intermediate load emissions rate for natural gas-fired combustion turbines
HIER_A | 120 | Heat input-based emissions rate of the actual fuel burned in the combustion turbine (lb CO2/MMBTU) - HHV Basis
HIER_NG | 120 | Heat input based emissions rate of natural gas (lb CO2 / MMBTU)